Novema kulde as bruker instruks

Side 21

Alarmkoder.

Feilkode	Årsak	Løsning	Action	Reset	alarm

rele

Check the correct supply of water to the cylinder; Turn the machine off and clean: the cylinder, the level control and the fi ll electrovalve

Turn the machine off and clean the water conductivity measuring electrodes;

If the problem persists, change the source of the supply

water or install a suitable treatment system (demineralisation, even partial);

The problem will not be resolved by softening the supply water

|  | high conductivity of the supply water |
| --- | --- |

| manuell | only if EE appears during AR |
| --- | --- |

total	auto

shutdown	available	aktiv

contradiction of the fl oat

|  | - activation of safety thermostat - Klixon activation - the thp output is open | Check the earth current of the heaters, and if replace necessary. Manually reset the Klixon Problem dependent mainly on operation without water; Turn the machine off and, once it has cooled down, reactivate the thermostat on the cylinder cover after having cleaned the cylinder and the level control, checking the efficiency of the components; Check that the electrical and water connections are in order and that the machine is supplied correctly; It may be necessary to replace the PTC sensors if installed | not available | active if Et remain in order at least a minute. |
| --- | --- | --- | --- | --- |

|  | autotest failed; probable problems in: supply water, level control or electrovalve | Ensure that the machine is supplied with water; Turn the machine off and clean the level control and the fi ll valve | Manuell | active only on the second EP or after EE during AR |
| --- | --- | --- | --- | --- |

|  | - electrical power not available; on machine start-up no steam is produced or the water is not preheated - fl oat locked in high level position. | With the machine off and disconnected from mains power supply, check that there are no defective of malfunctioning electrical connections | Manuell | active only on the second EP or after EE during AR |
| --- | --- | --- | --- | --- |

|  | No water | Check that the supply pipe from the water supply to the humidifi er and the internal pipe is not blocked or choked and that the pressure is suffi cient (1-8 bar); Check the operation of the fi ll electrovalve; Check that the steam supply does not have to work against excessive back-pressure, preventing the flow of water into the cylinder due to gravity; Check that the steam supply pipe is not choked or that there are no pockets of condensation | humidifi er disabled after waiting 10 min the alarm is automatically reset and a new fi ll cycle is attempted | manual or automatic (if after waiting 10 min the water supply returns) |
| --- | --- | --- | --- | --- |

Novema kulde as bruker instruks

Side 22

Feilkode	Årsak	Løsning	Action	Reset	alarm rele

|  | formation of foam in the cylinder during boiling | The formation of foam is usually due to the presence of surfactants in the water (lubricants, solvents, detergents, water treatment or softening agents) or an excessive concentration of dissolved salts. Drain the water supply line; Clean the cylinder | signal only Manuell not active |
| --- | --- | --- | --- |

|  | high water conductivity pre-alarm | Check the conductivity of the supply water; If necessary, install a suitable water treatment system; The problem will not be resolved by softening the supply water | humidifi er disabled | auto active availbale |
| --- | --- | --- | --- | --- |

low ambient humidity low temperature in T control)

signal only	auto

active

availbale

check the operation of the probe and the limit set by

parameter P3

internal memory error

Contact the CAREL service department	humidifi er	reprogram

active

disabled	CAREL

not active

manual hour counter reset

hour counter saving disabled

hour counter error Reset the hour counter (see Resetting the hour counter)

humidifi er disabled

room probe not connected

auto

active

available

Check the connection of the probe and the setting of parameter A0 for ON/OFF confi guration (see Reading and programming the parameters)

humidifi er disabled

outlet probe not connected (if featured)

auto

active

available

Check the pre-heating operation and the setting of parameters b1, b2, b3 (see Reading and programming the parameters);

Check the connections to the terminal block on the cylinder cover

pre heating disabled

NTC probe for measuring the water Temperature not connected (if featured)

auto

active

available

Check the pre-heating operation and the setting of parameters b1, b2, b3 (see Reading and programming the parameters);

Check the connections to the terminal block on the cylinder cover

regular maintenance signal

sigmal only	manual	not active

Stop the machine and carry out a complete maintenance routine on the humidifi er, resetting the hour counter (see

Resetting the hour counter)

active on the second “Ed”

manual

see

procedure “AR”

no drain pre-alarm or filter blocked

Check the drain valve/pump;

Check if the pipes or the manifold are blocked; Check if the level sensor is faulty or the pipes are blocked;

The filter inside the boiler may be clogged.

high outlet	auto

humidity	Check the operation of the outlet probe	signal only	availbale	active

user parameter error

With the machine off check that there are no defective or malfunctioning electrical connections

humidifi er disabled

parameters active

reprogram

|  | high ambient humidity (high temperature in T control) |  | Check the operation of the probe and the limit signal only auto active set by parameter P2 availbale |
| --- | --- | --- | --- |
|  |  | boiler full of water with no humidifi cation demand pre-alarm | Check if the fill valve is leaking; not Check if the high level sensor is dirty. signal only auto available active |

the humidifier does not turn on

the humidifier does not start operation

the humidifier wets the duct

Novema kulde as bruker instruks

Side 23

Feilsøking

Problem	Årsak	Løsning

- no electrical power; - external switch of the humidifier in position 0 (open); - control connectors badly connected; - broken fuses; - transformer fault

- remote ON/OFF contact open (relay/terminals AB – AB or 7I – 8I); - the humidistat has not been connected correctly; - humidistat fault - control signal not compatible with the type set - value measured by the probe/s higher than the corresponding set point

- too high steam inlet counterpressures;

the humidifier loads up water without producing steam

inlet filter to the clogged cylinder;

- limestone in the supply tank;

- drain solenoid valve malfunction

- thermal-magnetic overload switch is underrated - over-current at the electrodes

- the distributor is not installed correctly (too near the top of the duct or the condensate return is blocked); - system over-sized; - humidifier active when the fan in the duct is off

the thermal-magnetic overload

switch is activated

the humidifier wets the floor below

the humidifier drain is blocked;

- the supply water or overflow circuit has leaks;

- the condensate drain pipe does not bring the water back to the supply tank;

- the steam outlet pipe is not properly fastened to the cylinder

- check the protection devices upstream from the humidifier and the presence of power;

- close the switch on the panel: position I;

- check that the connectors are properly inserted in the terminal block;

- check the condition of fuses F1/F2/F3;

- check that the voltage across the secondary winding of the transformer is 24Vac

- close ON/OFF contacts (relay/terminals AB – AB or 7I – 8I);

- check the external connection;

- replace the humidistat

- set parameters A0, A2-A9 correctly

- check the values of the set point St and P7

- check that the steam inlet pipe is not folded or choked;

- clean the filter;

- clean supply tank;

- check the anomalous presence of 24Vac on drain solenoid valve and/or drain solenoid replacement

- check that the thermal-magnetic overload switch is rated for a current of at least 1.5 times the rated current of the humidifier

- see description for alarm EH

- check that the steam distributor is nstalled correctly;

- decrease the steam production set on the control;

- check the connection of the device (flow switch or differential pressure switch) slaving the humidifier to the ventilation in the duct (terminals AB - AB or 7I – 8I)

- clean the drain in the bottom tank;

- check the entire water circuit;

- check the correct position of the condensate drain pipe in the supply tank;

- check the fastening of the pipe clamps on the steam outlet